## SUGAR MCC'S-1
MOTOR LIST FOR SUGAR SECTION ( MCC / VFD PANEL) -ALL ARE NEW WITH IEC 60439.(FUSE LESS SYSTEM)
07.08.19 (REV-03)
MCC 1- CANE PREPARATION PANEL.
Sr No | EQUIPMENT NAME | TOTAL QTY | WORKING LOAD | STANDBY LOAD | KW | TYPE OF MOTOR | RPM | TYPE OF STARTER | REMARK |  |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | CANE UNLOADER THREE MOTION TROLLY -3 NOS | 1 | 1 | 0 | 118 | CRANE DUTY | 1000 | SUPPLY FEEDER | 250A MCCB | 0 |  |  | 118 | 0 |  |  | IE3
2 | CANE CHOPPER (NEW) | 1 | 1 | 0 | 160 | SQ. CAGE | 1500 | STAR /DELTA |  | 1 |  |  | 160 | 0 |  |  | IE3
3 | CANE LEVELLER | 1 | 1 | 0 | 187 | SLIPRING | 600 | DOL +FCMA |  | 1 |  |  | 187 | 0 |  |  | IE3
4 | MILL ROLLER LATHE | 1 | 0 | 1 | 15 | TEFC sq cage | 1500 | DOL |  | 1 |  |  | 0 | 15 |  |  | IE3
5 | FIBRIZER OIL PUMP PANEL | 1 | 1 |  | 5.5 |  |  | SUPPLY FEEDER | 3PH + N ,32A MCCB |  |  |  | 5.5 | 0 |  |  | IE3
6 | CONTROL SUPPLY FOR FCMA | 3 | [5 empty] | SUPPLY FEEDER | P+N ,32 DP MCB
7 | 75 KVAR CAPACITOR FEEDER | 2 | [5 empty] | DOL | WITH PB & TIMER
8 | SPARE FEEDER 1 | 1 |  |  | 160 |  |  | STAR /DELTA
9 | SPARE FEEDER 2 | 1 |  |  | 187 |  |  | DOL +FCMA
10 | PLUG SOCKET | 1 |  |  | 0
11 | CONTROL TRANSFORMER | 2 |  |  | 0
12 | INCOMMER FEEDER | 15 | [6 empty] | 1250 AMP, MDO ACB |  |  |  | 470.5 | 15 | 818.2609 | 981.913
| CAPACITOR bank | 150 KVAR | SUPPLIER SCOPE
MCC 2- MILL HOUSE MCC PANEL
Sr No | EQUIPMENT NAME | TOTAL QTY | WORKING LOAD | STANDBY LOAD | KW | TYPE OF MOTOR | RPM | TYPE OF STARTER | REMARK |  |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | IMBIBITION JUICE PUMP FOR MILL -1 TO 4 | 4 | 2 | 2 | 7.5 | TEFC sq cage | 1440 | DOL | 2W+2S (NEW) | 4 | 18 |  | 15 | 15 |  |  | IE3
2 | UNSCREENED JUICE PUMP -01 & 02 | 2 | 1 | 1 | 9.3 | TEFC sq cage | 960 | DOL | 1W+1S | 2 |  |  | 9.3 | 9.3 |  |  | IE3
3 | SCREENED JUICE PUMP-01 & 02 | 2 | 1 | 1 | 55 | TEFC sq cage | 1500 | STAR /DELTA | 1W+1S | 2 |  |  | 55 | 55 |  |  | IE3
4 | IMBIBTION WATER PUMP -01 & 02 | 2 | 1 | 1 | 18.5 | TEFC sq cage | 1500 | DOL |  | 2 |  |  | 18.5 | 18.5 |  |  | IE3
5 | RAKE TYPE INTER CARRIER ( FROM 2ND MILL TO 3RD MILL & 3RD MILL TO 1ST MILL) | 2 | 2 | 0 | 18.5 | TEFC sq cage | 1500 | DOL |  | 2 |  |  | 37 | 0 |  |  | IE3
| RAKE TYPE INTER CARRIER | 1 | 1 | 0 | 30 | TEFC sq cage | 1500 | DOL |  | 1 |  |  | 30 | 0
6 | MILL HYDRAULIC MOTOR | 1 | 1 | 0 | 11 | TEFC sq cage | 1500 | DOL |  | 1 |  |  | 11 | 0 |  |  | IE3
7 | MILL HOUSE CRANE | 1 | 1 | 0 | 22.4 | CRANE DUTY | 1000 | SUPPLY FEEDER | 100 A,MCCB | 0 |  |  | 22.4 | 0 |  |  | IE3
8 | MILL LUBRICATOR | 4 | 4 | 0 | 15 | TEFC sq cage | 1500 | DOL | 3PH + N | 4 |  |  | 60 | 0 |  |  | IE3
9 | MILL PLANATORY GEAR BOX OIL PUMP I ST MILL | 1 | 1 | 0 | 3.7 | TEFC sq cage | 1500 | DOL |  | 1 |  |  | 3.7 | 0 |  |  | IE3
10 | 50 KVAR CAPACITOR FEEDER | 1 | [5 empty] | DOL | WITH PB & TIMER
11 | MILL HOUSE AIR CONDITIONING | 4 | [5 empty] | SUPPLY FEEDER | 32 A, MCCB
12 | SPARE STARTER FEEDER 1 | 1 |  |  | 18.5 |  |  | DOL
13 | SPARE STARTER FEEDER 2 | 1 |  |  | 55 |  |  | DOL
14 | SPARE STARTER FEEDER 3 | 1 |  |  | 9.3 |  |  | DOL
15 | PLUG SOCKET | 1 |  |  | 0 |  |  | 63A
16 | CONTROL TRANSFORMER | 2 |  |  | 0
17 | INCOMMER FEEDER | 31 | [6 empty] | 630AMP ,MCCB |  |  |  | 261.9 | 97.8 | 455.4783 | 546.5739
| CAPACITOR BANK | 50 KVAR | SUPPLIER SCOPE
MCC 3- CLARIFICATION HOUSE
Sr No | EQUIPMENT NAME | TOTAL QTY | WORKING LOAD | STANDBY LOAD | KW | TYPE OF MOTOR | RPM | TYPE OF STARTER | REMARK |  |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | PHOSPHATE TANK | 1 | 1 | 0 | 2.2 | TEFC sq cage | 1440 | DOL |  | 1 | 56 |  | 2.2 | 0 |  |  | IE3
2 | PHOSPHATE DOSING PUMP | 1 | 1 | 0 | 0.37 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 0.37 | 0 |  |  | IE3
3 | JUICE SULPHITOR DRIVE | 1 | 1 | 0 | 11 | TEFC sq cage | 960 | DOL |  | 1 |  |  | 11 | 0 |  |  | IE3
4 | PUMP FOR FILTRATE RECEVING TANK | 4 | 4 | 0 | 3.7 | TEFC sq cage | 1440 | DOL |  | 4 |  |  | 14.8 | 0 |  |  | IE3
5 | AIR COMPRESSORS | 2 | 1 | 1 | 30 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 30 | 30 |  |  | IE3
6 | LIQUIDATING PUMP | 2 | 1 | 1 | 7.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 7.5 | 7.5 |  |  | IE3
7 | GRIT SCREW CONVEYER /GRIT CATCHER | 1 | 1 | 0 | 1.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 1.5 | 0 |  |  | IE3
8 | INSTRUMENTATION AIR COMPRESSORS | 1 | 1 | 0 | 5.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 5.5 | 0 |  |  | IE3
| CLEAR JUICE PUMP | 2 | 1 | 1 | 55 | TEFC sq cage |  | S/D |  | 2 |  |  | 55 | 55 |  |  | IE3
10 | M.O.L PREPARATION PUMP | 2 | 1 | 1 | 3.75 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 3.75 | 3.75 |  |  | IE3
11 | MUD OVER FLOW PUMP | 2 | 1 | 1 | 3.7 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 3.7 | 3.7 |  |  | IE3
12 | LIME CLASSIFIER | 1 | 1 | 0 | 3.7 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 3.7 | 0 |  |  | IE3
13 | VACCUM FILTER DRIVE | 2 | 1 | 1 | 1.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 1.5 | 1.5 |  |  | IE3
14 | AIR COMPRESSORS FOR SULPHER BURNER 400 M3 | 2 | 1 | 1 | 15 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 15 | 15 |  |  | IE3
15 | VACUMM PUMP700 M3 | 2 | 1 | 1 | 22.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 22.5 | 22.5 |  |  | IE3
16 | AGITATOR | 2 | 1 | 1 | 0.75 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 0.75 | 0.75 |  |  | IE3
| WASH WATER PUMP | 2 | 1 | 1 | 2.2 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 2.2 | 2.2 |  |  | IE3
17 | MUD FILTER | 1 | 1 | 0 | 1.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 1.5 | 0 |  |  | IE3
18 | MUD CLARIFIER | 1 | 1 | 0 | 1.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 1.5 | 0 |  |  | IE3
19 | CAKE WASH WATER PUMP | 2 | 1 | 1 | 3.7 | TEFC sq cage | 2900 | DOL |  | 2 |  |  | 3.7 | 3.7 |  |  | IE3
20 | BAGACILLO BLOWER | 1 | 1 | 0 | 11.1 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 11.1 | 0 |  |  | IE3
21 | MUD BELT CONVEYOR | 1 | 1 | 0 | 1.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 1.5 | 0 |  |  | IE3
22 | FEED MIXER | 1 | 1 | 0 | 1.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 1.5 | 0 |  |  | IE3
23 | MUD RECIRCULATION PUMP | 1 | 1 | 0 | 3.7 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 3.7 | 0 |  |  | IE3
24 | LIME SLACKER | 1 | 1 | 0 | 3.7 | TEFC sq cage | 960 | DOL |  | 1 |  |  | 3.7 | 0 |  |  | IE3
25 | MOL. LIME TANK DRIVE | 2 | 1 | 1 | 3.7 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 3.7 | 3.7 |  |  | IE3
26 | CLEAR JUICE PUMP FOR FILTER PRESS | 1 | 1 | 0 | 1.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 1.5 | 0 |  |  | IE3
27 | SULPHUR BURNER FOR JUICE SULPHITATION | 2 | 1 | 1 | 1.1 | TEFC sq cage | 950 | DOL |  | 2 |  |  | 1.1 | 1.1 |  |  | IE3
28 | SULPHUR BURNER FOR SYRUP SULPHITATION | 2 | 1 | 1 | 1.1 | TEFC sq cage | 950 | DOL |  | 2 |  |  | 1.1 | 1.1 |  |  | IE3
29 | AIR DRYER (DEHUMIDIFIER) | 2 | 1 | 1 | 1.5 | TEFC sq cage | 950 | DOL |  | 2 |  |  | 1.5 | 1.5 |  |  | IE3
30 | AIR BLOWER FOR SULPHUR BURNER (JUICE) | 2 | 1 | 1 | 3.7 | TEFC sq cage | 950 | DOL |  | 2 |  |  | 3.7 | 3.7 |  |  | IE3
31 | AIR BLOWER FOR SULPHUR BURNER (SYRUP) | 2 | 1 | 1 | 3.7 | TEFC sq cage | 950 | DOL |  | 2 |  |  | 3.7 | 3.7 |  |  | IE3
32 | TREATED JUICE PUMP | 2 | 1 | 1 | 5.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 5.5 | 5.5 |  |  | IE3
34 | FILTERED CLEAR JUICE PUMP | 2 | 1 | 1 | 18.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 18.5 | 18.5 |  |  | IE3
35 | Sulphur Burner Heating element control panel , 100kg / Hr, 2KWx14nos | 1 | 1 | 0 | 28 |  |  | SUPPLY FEEDER | 63 A, MCCB,NEW FILTER MOTOR |  |  |  | 28 | 0 |  |  | IE3
36 | AUTO PH CONTROL SYSTEM | 1 | 1 | 0 | 2 |  |  | SUPPLY FEEDER | 32 A, MCCB,NEW FILTER MOTOR |  |  |  | 2 | 0 |  |  | IE3
37 | 75 KVAR CAPACITOR FEEDER | 1 | [5 empty] | DOL | WITH PB & TIMER |  |  |  | 0 | 0
38 | PLUG SOCKET | 1 | [6 empty] | 63 A,MCCB |  |  |  | 0 | 0
39 | SPARE STARTER FEEDER 1 | 1 |  |  | 30 |  |  | DOL |  |  |  |  | 0 | 0
40 | SPARE STARTER FEEDER 2 | 1 |  |  | 18.5 |  |  | DOL |  |  |  |  | 0 | 0
41 | SPARE STARTER FEEDER 3 | 1 |  |  | 11 |  |  | DOL |  |  |  |  | 0 | 0
| SPARE STARTER FEEDER 4 | 1 |  |  | 5.5 |  |  | DOL |  |  |  |  | 0 | 0
| SPARE STARTER FEEDER 5 | 1 |  |  | 1.5 |  |  | DOL
| SPARE STARTER FEEDER 5 | 1 |  |  | 55 |  |  | S/D
42 | CONTROL TRANSFORMER | 2 | [10 empty] | 0 | 0
4 | INCOMMER FEEDER | [7 empty] | 630 AMP ,MCCB |  |  |  | 279.47 | 184.4 | 486.0348 | 583.2417
| CAPACITOR BANK | 75 KVAR | SUPPLIER SCOPE
MCC 4 -EVAPORATION STATION MCC PANEL
Sr No | EQUIPMENT NAME | TOTAL QTY | WORKING LOAD | STANDBY LOAD | KW | TYPE OF MOTOR | RPM | TYPE OF STARTER | REMARK |  |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | CONDENSATE PUMP FOR JH ( 1 TO 5) | 5 | 5 | 0 | 3.7 | TEFC sq cage | 1440 | DOL |  | 5 | 35 |  | 18.5 | 0 |  |  | IE3
2 | WEIGHED JUICE PUMP | 1 | 1 | 0 | 75 | TEFC sq cage | 1440 | S/D |  | 1 |  |  | 75 | 0 |  |  | IE3
3 | WEIGHTED MIXED JUICE PUMP - NEW | 2 | 1 | 1 | 90 | TEFC sq cage | 1440 | S/D |  | 2 |  |  | 90 | 90 |  |  | IE3
4 | PUMP FOR CHECK WEIGHING SCALE | 1 | 1 | 0 | 2.2 | TEFC sq cage | 960 | DOL |  | 1 |  |  | 2.2 | 0 |  |  | IE3
5 | CONDENSATE PUMP FOR VLJH ( 1 TO 2) | 2 | 1 | 1 | 2.2 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 2.2 | 2.2 |  |  | IE3
6 | DOSING PUMP | 1 | 1 | 0 | 0.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 0.5 | 0 |  |  | IE3
7 | FILTERED CLEAR JUICE PUMP | 2 | 1 | 1 | 18.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 18.5 | 18.5 |  |  | IE3
8 | COND. EXTRACTION PUMP FOR 1 & 2 QUAD | 2 | 1 | 1 | 7.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 7.5 | 7.5 |  |  | IE3
9 | COND. EXTRACTION PUMP FOR 3 & 4 QUAD | 2 | 1 | 1 | 3.7 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 3.7 | 3.7 |  |  | IE3
10 | COND. EXTRACTION PUMP FOR VC | 2 | 1 | 1 | 2.2 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 2.2 | 2.2 |  |  | IE3
11 | SYRUP EXTRACTION PUMP -1 & 2 | 2 | 1 | 1 | 18.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 18.5 | 18.5 |  |  | IE3
12 | COND. EXTRACTION PUMP | 2 | 1 | 1 | 7.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 7.5 | 7.5 |  |  | IE3
13 | SUPHITED SYRUP PUMP | 2 | 1 | 1 | 18.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 18.5 | 18.5 |  |  | IE3
14 | DRIVE FOR PHOSPHATE STORING | 1 | 1 | 0 | 2.2 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 2.2 | 0 |  |  | IE3
15 | PHOSPHATE SLURRY PUMP | 2 | 1 | 1 | 2.2 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 2.2 | 2.2 |  |  | IE3
16 | OIL SKIMMER MOTOR | 1 | 1 | 0 | 0.75 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 0.75 | 0 |  |  | IE3
17 | SYRUP TRANSFER PUMP | 2 | 1 | 1 | 11.1 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 11.1 | 11.1 |  |  | IE3
18 | CLEAR JUICE TRANSFER PUMP | 2 | 1 | 1 | 15 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 15 | 15 |  |  | IE3
19 | COND. PUMP FOR JH CLEAR JUICE | 2 | 1 | 1 | 3.7 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 3.7 | 3.7 |  |  | IE3
20 | 75 KVAR CAPACITOR FEEDER | 1 | [5 empty] | DOL | WITH PB & TIMER |  |  |  | 0 | 0
21 | SPARE FEEDER 1 | 1 |  |  | 18.5 |  |  | DOL |  |  |  |  | 0 | 0
22 | SPARE FEEDER 2 | 1 |  |  | 90 |  |  | S/D |  |  |  |  | 0 | 0
23 | SPARE FEEDER 3 | 1 |  |  | 3.7 |  |  | DOL |  |  |  |  | 0 | 0
24 | PLUG SOCKET | 1 | [6 empty] | 63 A, MCCB |  |  |  | 0 | 0
25 | CONTROL TRANSFORMER | 2 | [10 empty] | 0 | 0
10 | INCOMMER FEEDER | 43 |  |  |  |  | - |  | 800AMP, ACB |  |  |  | 299.75 | 200.6 | 521.3043 | 625.5652
| CAPACITOR BANK | 75 KVAR | SUPPLIER SCOPE
MCC 7 - CRYSTALIZER MCC PANEL
Sr No | EQUIPMENT NAME | TOTAL QTY | WORKING LOAD | STANDBY LOAD | KW | TYPE OF MOTOR | RPM | TYPE OF STARTER | REMARK |  |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | CAUSTIC SODA TANK (AIR COOLED CRYSTALLIZER SODA TANK) | 1 | 1 | 0 | 3.7 | TEFC sq cage | 1440 | DOL |  | 1 | 41 |  | 3.7 | 0 |  |  | IE3
2 | MOLASSES CONDITIONER - AH1 &BH 2, CL3 | 3 | 3 | 0 | 7.5 | TEFC sq cage | 1440 | DOL |  | 3 |  |  | 22.5 | 0 |  |  | IE3
3 | CONDENSATE PUMP FOR VAPOUR | 2 | 1 | 1 | 5.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 5.5 | 5.5 |  |  | IE3
4 | CONDENSATE PUMP FOR EXHAUST | 2 | 1 | 1 | 15 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 15 | 15 |  |  | IE3
5 | SEED CRYSTALLIZER | 1 | 1 | 0 | 7.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 7.5 | 0 |  |  | IE3
6 | SEED ELEVATOR | 1 | 1 | 0 | 5.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 5.5 | 0 |  |  | IE3
7 | DRY SEED CRYSTALLIZER | 1 | 1 | 0 | 7.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 7.5 | 0 |  |  | IE3
8 | VACCUM CRYSTALLIZER - ABC | 3 | 3 | 0 | 7.5 | TEFC sq cage | 1440 | DOL |  | 3 |  |  | 22.5 | 0 |  |  | IE3
9 | AIR COOLED CRYSTALLIZER B | 1 | 1 | 0 | 11 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 11 | 0 |  |  | IE3
10 | AIR COOLED CRYSTALLIZER - 65 T B1 (NEW) | 1 | 1 | 0 | 15 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 15 | 0 |  |  | IE3
11 | AIR COOLED CRYSTALLIZER - 65 T B2 | 2 | 1 | 1 | 15 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 15 | 15 |  |  | IE3
12 | VERTICAL CONT,. CRYT. 180 T | 1 | 1 | 0 | 15 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 15 | 0 |  |  | IE3
13 | VERTICAL CONT,. CRYT. 450 T | 2 | 1 | 1 | 18.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 18.5 | 18.5 |  |  | IE3
14 | 75 KVAR CAPACITOR FEEDER | 1 | [5 empty] | DOL | WITH PB & TIMER |  |  |  | 0 | 0
15 | SPARE STARTER FEEDER 1 | 1 |  |  | 18.5 |  |  | DOL |  |  |  |  | 0 | 0
16 | SPARE STARTER FEEDER 2 | 1 |  |  | 11 |  |  | DOL |  |  |  |  | 0 | 0
17 | SPARE STARTER FEEDER 3 | 1 |  |  | 3.7 |  |  | DOL |  |  |  |  | 0 | 0
18 | PLUG SOCKET | 1 | [6 empty] | 63 A, MCCB |  |  |  | 0 | 0
19 | CONTROL TRANSFORMER | 2 | [10 empty] | 0 | 0
20 | INCOMMER FEEDER | 28 |  |  |  |  | - |  | 630AMP, MCCB |  |  |  | 164.2 | 33.5 | 285.5652 | 342.6783
| CAPACITOR BANK | 75 KVAR | SUPPLIER SCOPE
MCC 5- PAN & CURING HOUSE MCC PANEL
Sr No | EQUIPMENT NAME | TOTAL QTY | WORKING LOAD | STANDBY LOAD | KW | TYPE OF MOTOR | RPM | TYPE OF STARTER | REMARK |  |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | WATER COOLED CRYSTALLIZER 65 T FOR MASS 'ABC MASSCUITE' | 3 | 3 | 0 | 11 | TEFC sq cage | 1440 | DOL |  | 3 |  |  | 33 | 0 |  |  | IE3
2 | MOLASSES PUMP FOR A | 3 | 3 | 0 | 30 | TEFC sq cage | 1440 | DOL |  | 3 |  |  | 90 | 0 |  |  | IE3
3 | MOLASSES PUMP FOR B | 2 | 1 | 1 | 15 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 15 | 15 |  |  | IE3
4 | MOLASSES PUMP FOR C | 2 | 1 | 1 | 15 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 15 | 15 |  |  | IE3
5 | VERTICAL CONT,. CRYT. 180 T | 1 | 1 | 0 | 15 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 15 | 0 |  |  | IE3
6 | VERTICAL CONT,. CRYT. 450 T | 2 | 1 | 1 | 18.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 18.5 | 18.5 |  |  | IE3
7 | B & C LIQUIDATION PUMPS | 2 | 1 | 1 | 11 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 11 | 11 |  |  | IE3
8 | COLD WATER PUMP | 2 | 1 | 1 | 7.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 7.5 | 7.5 |  |  | IE3
9 | HOT WATER PUMP | 2 | 1 | 1 | 7.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 7.5 | 7.5 |  |  | IE3
10 | VACCUM PUMP | 1 | 1 | 0 | 15 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 15 | 0 |  |  | IE3
11 | MELT PUMP | 2 | 1 | 1 | 18.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 18.5 | 18.5 |  |  | IE3
12 | SUGAR MELTER | 1 | 1 | 0 | 5.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 5.5 | 0 |  |  | IE3
13 | 75 KVAR CAPACITOR FEEDER | 1 |  |  | 18.5 |  |  | DOL | WITH PB & TIMER |  |  |  | 0 | 0
14 | SPARE STARTER FEEDER 1 | 1 |  |  | 30 |  |  | DOL |  |  |  |  | 0 | 0
15 | SPARE STARTER FEEDER 2 | 1 |  |  | 7.5 |  |  | DOL |  |  |  |  | 0 | 0
16 | SPARE STARTER FEEDER 3 | 1 | [10 empty] | 0 | 0
17 | PLUG SOCKET | 1 | [6 empty] | 63 A, MCCB |  |  |  | 0 | 0
18 | CONTROL TRANSFORMER | 2 | [10 empty] | 0 | 0
19 | INCOMMER FEEDER | 30 |  |  |  |  | - |  | 630AMP, MCCB |  |  |  | 251.5 | 93 | 437.3913 | 524.8696
| CAPACITOR BANK | 75 KVAR | SUPPLIER SCOPE
MCC 6 - CENTRIFUGAL STATION MCC PANEL
Sr No | EQUIPMENT NAME | TOTAL QTY | WORKING LOAD | STANDBY LOAD | KW | TYPE OF MOTOR | RPM | TYPE OF STARTER | REMARK | PUSH BUTTON QTY |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | PUG MILL FOR A C/F MACHINE | 2 | 1 | 1 | 3.7 | TEFC sq cage | 1440 | DOL |  | 2 | 27 |  | 3.7 | 3.7 |  |  | IE3
2 | SUPERHEATED WASH WATER PUMP | 2 | 1 | 1 | 15 | TEFC sq cage | 2900 | DOL |  | 2 |  |  | 15 | 15 |  |  | IE3
3 | WATER HEATER FOR C/F MACHINE | 1 | 1 | 0 | 3.7 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 3.7 | 0 |  |  | IE3
4 | COMPRESSOR FOR C/F | 2 | 1 | 1 | 15 | TEFC sq cage | 1440 | S/D |  | 2 |  |  | 15 | 15 |  |  | IE3
5 | MOLASSES PUMP FOR AH | 2 | 1 | 1 | 7.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 7.5 | 7.5 |  |  | IE3
6 | MOLASSES PUMP FOR AL | 2 | 1 | 1 | 7.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 7.5 | 7.5 |  |  | IE3
7 | PUG MILL FOR FLAT BOTTOM C/F(A) | 1 | 1 | 0 | 3.7 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 3.7 | 0 |  |  | IE3
8 | MAGAMA MIXTURE FOR CF | 1 | 1 | 0 | 5.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 5.5 | 0 |  |  | IE3
9 | MAGAMA MIXTURE FOR B&C | 2 | 1 | 1 | 5.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 5.5 | 5.5 |  |  | IE3
10 | MAGAMA PUMP FOR CF | 1 | 1 | 0 | 7.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 7.5 | 0 |  |  | IE3
11 | B/CA-MAGMA PUMP | 2 | 1 | 1 | 7.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 7.5 | 7.5 |  |  | IE3
12 | CH-MOLASSES PUMP | 2 | 1 | 1 | 5.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 5.5 | 5.5 |  |  | IE3
13 | CL-MOLASSES PUMP | 1 | 1 | 0 | 5.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 5.5 | 0 |  |  | IE3
14 | BH MOLASSES PUMP | 1 | 1 | 0 | 5.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 5.5 | 0 |  |  | IE3
15 | CAUSTIC SODA PUMP | 1 | 1 | 0 | 7.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 7.5 | 0 |  |  | IE3
16 | MAGAMA MIXTURE | 1 | 1 | 0 | 5.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 5.5 | 0 |  |  | IE3
17 | WEIGHTED MOLASSES PUMP | 2 | 1 | 1 | 11.19 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 11.19 | 11.19 |  |  | IE3
18 | FINAL MOLASSES PUMP BELOW MC | 1 | 1 | 0 | 11.19 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 11.19 | 0 |  |  | IE3
| SUPPLY FEEDER FOR SUGAR MCC PANEL | 1 | 1 | 0 | 107.25 |  |  | SUPPLY FEEDER |  |  |  |  | 107.25 | 0
19 | 75 KVAR CAPACITOR FEEDER | 1 | [5 empty] | DOL | WITH PB & TIMER |  |  |  | 0 | 0
20 | SPARE STARTER FEEDER 1 | 1 |  |  | 11.19 |  |  | DOL |  |  |  |  | 0 | 0
21 | SPARE STARTER FEEDER 2 | 1 |  |  | 15 |  |  | DOL |  |  |  |  | 0 | 0
22 | SPARE STARTER FEEDER 3 | 1 |  |  | 5.5 |  |  | DOL |  |  |  |  | 0 | 0
23 | CONTROL TRANSFORMER | 2 | [10 empty] | 0 | 0
24 | INCOMMER FEEDER | 34 |  |  |  |  | - |  | 630AMP, MCCB |  |  |  | 241.23 | 78.39 | 419.5304 | 503.4365
| CAPACITOR BANK | 75 KVAR | SUPPLIER SCOPE
MCC -7 -SUGAR HANDLING MCC PANEL
Sr No | EQUIPMENT NAME | TOTAL QTY | WORKING LOAD | STANDBY LOAD | KW | TYPE OF MOTOR | RPM | TYPE OF STARTER | REMARK |  |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | AUXILIARY AIR FANS | 2 | 2 | 0 | 1.5 | TEFC sq cage | 1440 | DOL |  | 2 | 15 |  | 3 | 0 |  |  | IE3
2 | SUGAR BUCKET ELEVATOR | 2 | 2 | 0 | 5.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 11 | 0 |  |  | IE3
3 | SUGAR GRADER | 2 | 2 | 0 | 7.5 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 15 | 0 |  |  | IE3
4 | SUPPLY FEEDER TO FINAL MOLASSES PUMP WEIGHING SCALE | [5 empty] | 1440 | SUPPLY FEEDER | 63 A, MCCB | 0 |  |  | 30 | 0 |  |  | IE3
5 | DRY SEED BELT CONVEYOR / SUAGAR BELT CONVEYOR TO SUGAR ELEVATOR | 1 | 1 | 0 | 7.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 7.5 | 0 |  |  | IE3
6 | MULTI TRAY GRASS HOPPER | 3 | 3 | 0 | 11.19 | TEFC sq cage | 1440 | DOL |  | 3 |  |  | 33.57 | 0 |  |  | IE3
7 | MOLASSES RECIRCULATION PUMP | 2 | 2 | 0 | 11.19 | TEFC sq cage | 1440 | DOL |  | 2 |  |  | 22.38 | 0 |  |  | IE3
8 | DRY SEED MAGMA PUMP | 1 | 1 | 0 | 11.1 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 11.1 | 0 |  |  | IE3
9 | DRY SEED MAGMA MIXTURE | 1 | 1 | 0 | 3.7 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 3.7 | 0 |  |  | IE3
10 | SPARE STARTER FEEDER 1 | 1 |  |  | 11.19 |  |  | DOL |  |  |  |  | 0 | 0
11 | SPARE STARTER FEEDER 2 | 1 |  |  | 7.5 |  |  | DOL |  |  |  |  | 0 | 0
12 | SPARE STARTER FEEDER 3 | 1 |  |  | 1.5 |  |  | DOL |  |  |  |  | 0 | 0
13 | CONTROL TRANSFORMER | 2 | [10 empty] | 0 | 0
14 | INCOMMER FEEDER | 19 |  |  |  | - | - | INCOMMER FEEDER | 400 AMP ,MCCB |  |  |  | 137.25 | 78.39 | 238.6957 | 286.4348
| Capacitor BANK | 25 kvar | Supplier scope
MCC - 8 - Continuous centrifugal (CF)
Sr No | Equipement Name | KW | WORKING LOAD | STANDBY LOAD | HP | Qty | Type of motor | RPM | Type of starter |  |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | continuous type Centrifugal machine for 'C - Fore worker Masscuite | 55 |  |  | 75 | 4 | TEFC SQ CAGE | 1440 | ASD | 4 | 4 |  | 220 | 0 |  |  | IE3
| SPARE STARTER FEEDER | 55 |  |  |  | 1 |  |  | ASD
2 | INCOMMER FEEDER |  |  |  |  | - | - |  | 800 AMP, MDO ACB |  |  |  | 220 | 0 | 382.6087 | 459.1304
MCC -9 - Continuous centrifugal (C A B)
Sr No | Equipement Name | KW | WORKING LOAD | STANDBY LOAD | HP | Qty | Type of motor | RPM | Type of starter |  |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | continuous type Centrifugal machine for 'B AFTER & C AFTER - worker Masscuite | 55 |  |  | 75 | 3 | TEFC SQ CAGE | 1440 | ASD | 3 | 3 |  | 165 | 0 |  |  | IE3
2 | continuous type Centrifugal machine for C AFTER - worker Masscuite -NEW | 55 |  |  | 75 | 1 | TEFC SQ CAGE | 1440 | ASD | 1 | 1 |  | 55 | 0 |  |  | IE3
| SPARE STARTER FEEDER | 55 |  |  |  | 1 |  |  | ASD
3 | INCOMMER FEEDER |  |  |  |  | - | - |  | 800 AMP, MDO ACB |  |  |  | 220 | 0 | 382.6087 | 459.1304
** | EFFLUIENT TREATMENT PLANT -MCC 10
Sr No | Equipment Name | Qty |  |  | KW | Type of Motor | RPM | Type of Starter | Remark |  |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | Primary Clarifier | 3 |  |  | 11 | TEFC sq cage | 1450 | DOL |  | 3 | 6 |  | 33 | 0 |  |  | IE3
2 | Fixed Aerators | 1 |  |  | 11 | TEFC sq cage | 1450 | DOL |  | 1 |  |  | 11 | 0 |  |  | IE3
3 | Floating Aerator | 1 |  |  | 11 | TEFC sq cage | 1450 | DOL |  | 1 |  |  | 11 | 0 |  |  | IE3
4 | Secondary Clarifier | 1 |  |  | 11 | TEFC sq cage | 1450 | DOL |  | 1 |  |  | 11 | 0 |  |  | IE3
5 | INCOMMER FEEDER |  |  |  | 66.6 |  |  |  | 315 AMP, MCCB |  | 206 | 0 | 66 | 0 | 114.7826 | 137.7391
** | FINAL MOLASSES DB- MCC-11 | [8 empty] | PUSH BUTTON QTY
Sr No | Equipment Name | TOTAL QTY | WORKING LOAD | STANDBY LOAD | KW | TYPE OF MOTOR | RPM | TYPE OF STARTER | REMARK
1 | FINAL MOLASSES PUMP WEIGHING SCALE | 2 | 1 | 1 | 7.5 | TEFC sq cage | 1450 | DOL | EXSISTING | 2 | 6
2 | INCOMMER FEEDER | [7 empty] | 63A ,MCCB |  | 418 | 0
** | WORK SHOP DB-MCC-12
Sr No | Equipment Name | Qty |  |  | KW | Type of Motor | RPM | Type of Starter | Remark |  |  |  | WORKING LOAD | STANDBY LOAD | INCOMMER IN AMP(I) |  | Motor efficiency class
1 | LATHE MACHINE 8' BED LENGTH GAP TYPE | 1 |  |  | 5.5 | TEFC sq cage | 1450 | DOL |  | 1 | 6 |  | 5.5 | 0 |  |  | IE3
2 | LATHE MACHINE 10 ' BED LENGTH GAP TYPE | 1 |  |  | 5.5 | TEFC sq cage | 1450 | DOL |  | 1 | 6 |  | 5.5 | 0 |  |  | IE3
3 | SHAPING MACHINE MAX. STROKE 24" | 1 |  |  |  | TEFC sq cage | 1450 | DOL |  | 1 | 6 |  | 0 | 0 |  |  | IE3
4 | PLANNING MACHINE MAX. STROKE 8" | 1 |  |  |  | TEFC sq cage | 1450 | DOL |  | 1 | 6 |  | 0 | 0 |  |  | IE3
5 | PILLIAR DRILING MACHINE | 1 |  |  |  | TEFC sq cage | 1450 | DOL |  | 1 | 6 |  | 0 | 0 |  |  | IE3
6 | SAW CUTTING MACHINE | 1 |  |  |  | TEFC sq cage | 1450 | DOL |  | 1 | 6 |  | 0 | 0 |  |  | IE3
5 | INCOMMER FEEDER |  |  |  | 25 KW |  |  |  | 315 AMP, MCCB |  | 872 | 0 |  |  | 0 | 0
| MCC 13 - INJECTION WATER MCC PANEL | [8 empty] | PUSH BUTTON QTY
Sr No | EQUIPMENT NAME | TOTAL QTY | WORKING LOAD | STANDBY LOAD | KW | TYPE OF MOTOR | RPM | TYPE OF STARTER | REMARK |  |  |  | WORKING LOAD | STANDBY LOAD |  |  | Motor efficiency class
1 | INJECTION PUMP FOR VACCUM PAN (180HP SLIP RING) -1 1500 M3 | 3 | 2 | 1 | 132 | TEFC sq cage | 960 | DOL | FCMA | 1 | 4 |  | 264 | 132 |  |  | IE3
2 | INJECTION AIR EJECTOR 750 M3 | 3 | 2 | 1 | 75 | TEFC sq cage | 1440 | S/D |  | 3 |  |  | 150 | 75 |  |  | IE3
3 | SERVICE WATER PUMP | 2 | 1 | 1 | 30 | TEFC sq cage | 960 | DOL | FCMA | 1 | 4 |  | 30 | 30 |  |  | IE3
4 | PRIMING PUMP FOR INJECTION WATER PUMP | 1 | 1 | 0 | 7.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 7.5 | 0 |  |  | IE3
| INJECTION WATER PUMP | 1 | 1 | 0 | 1.5 | TEFC sq cage | 1440 | DOL
| INJECTION PUMP FOR EVAPORATORS | 1 | 1 | 0 | 45 | TEFC sq cage | 1440 | S/D |  |  |  |  | 45
5 | 75 KVAR CAPACITOR FEEDER | 2 | [5 empty] | DOL | WITH PB & TIMER |  |  |  | 0 | 0
6 | SPARE STARTER FEEDER 1 ,132 KW | 1 |  |  | 132 |  |  | DOL |  |  |  |  | 0 | 0
7 | SPARE STARTER FEEDER 2, 75 KW | 1 |  |  | 75 |  |  | S/D |  |  |  |  | 0 | 0
8 | CONTROL TRANSFORMER | 2 | [10 empty] | 0 | 0
9 | INCOMMER FEEDER |  |  |  |  | - | - | 1000AMP ,MDO ACB |  |  |  |  | 496.5 | 237
| CAPACITOR 150 KVAR | SUPPLIER SCOPE
MCC 14 - SPRAY WATER PUMP
Sr No | EQUIPMENT NAME | TOTAL QTY | WORKING LOAD | STANDBY LOAD | KW | TYPE OF MOTOR | RPM | TYPE OF STARTER | REMARK |  |  |  | WORKING LOAD | STANDBY LOAD |  |  | Motor efficiency class
1 | SPRAY WATER PUMP -1 2&,3 1100 M3/HR | 3 | 3 | 0 | 45 | TEFC sq cage | 960 | S/D |  | 3 | 5 |  | 135 | 0 |  |  | IE3
2 | SPRAY WATER PUMP -1 2000 M3/HR | 1 | 1 | 0 | 110 | TEFC sq cage | 960 | S/D |  | 1 |  |  | 110 | 0 |  |  | IE3
3 | PRIMING PUMP | 1 | 1 | 0 | 7.5 | TEFC sq cage | 1440 | DOL |  | 1 |  |  | 7.5 | 0 |  |  | IE3
4 | POWER SUPPLY TO RAW WATER PUMP AT RAW WATER STORAGE TANK | 2 | 2 | 0 | 22 | TEFC sq cage | 1440 | SUPPLY FEEDER-125A MCCB |  |  |  |  | 44 | 0 |  |  | IE3
| WATER HADLING PUMP | 1 | 1 | 0 | 30 | TEFC sq cage | 1440 | DOL |  |  |  |  | 30 | 0
| COLD WATER PUMP | 2 | 1 | 1 | 45 | TEFC sq cage | 960 | S/D |  |  |  |  | 45 | 45
5 | SPARE STARTER FEEDER 45 KW | 1 |  |  | 45 |  |  | S/D |  |  |  |  | 0 | 0
6 | SPARESTARTER FEEDER 110 KW | 1 |  |  | 110 |  |  | S/D |  |  |  |  | 0 | 0
7 | PLUG SOCKET | 1 | [10 empty] | 0 | 0
8 | CONTROL TRANSFORMER | 2 | [10 empty] | 0 | 0
9 | 75 KVAR CAPACITOR FEEDER | 1 |  |  |  |  | DOL | WITH PB & TIMER |  |  |  |  | 0 | 0
10 | INCOMMER FEEDER |  |  |  |  | - | - | 1000 AMP , MDO ACB |  |  |  |  | 371.5 | 45
| 75 KVAR CAPACITOR | SUPPLIER SCOPE
Push button station for non VFD motors - (DOL)
Sr No | Equipement Name | KW |  |  | HP | Type of motor | RPM | Qty | Type of starter
1 | Push button station IP 65 (Outdoor) with 1NO for On + 1NC | NA |  |  | NA | NA | NA | 250 | NA
Push button station for VFD motors
Sr No | Equipement Name | KW |  |  | HP | Type of motor | RPM | Qty | Type of starter
1 | The Remote Control Station shall be IP – 55 / 65 in VFD supplier’s scope, the remote push button shall have ammeter, RPM meter, On / off push button, speed raise, lower P.B., on off trip cluster type LED lamps etc | NA |  |  | NA | NA | NA | 12 | NA
Note: All panels shall have DCS hook up facility